## PS - Buddhist Gallery
ANNEXURE - 2
PROJECT : CSMVS, HVAC SYSTEM - SCHEDULE OF WORK - Proposed Buddhist Art Gallery
PRICE SUMMARY
A | TENDERED ITEMS
I | EQUIPMENTS | Rs.
II | AIR DISTRIBUTION | Rs.
III | INSULATION | Rs.
IV | ELECTRICAL | Rs.
V | MISCELLANEOUS | Rs.
| TOTAL FOR A | Rs.
VI | MAINTENANCE | Rs.
B | TAXES
I | CGST | Rs.
II | SGST | Rs.
| TOTAL FOR B | Rs.
| GRAND TOTAL (A+B) | Rs.

## Buddhist Gallery
ANNEXURE - 2
PROJECT : CSMVS, HVAC SYSTEM - SCHEDULE OF WORK - Proposed Buddhist Art Gallery
SR. | ITEM PARTICULARS | UNIT | QUANTITY | RATE INR To be filled by the contractor | AMOUNT
I | EQUIPMENTS
1 | VRF AIR-CONDITIONING SYSTEM (AIR COOLED)
VRF Airconditioning equipment as specified and shown on the drawing complete with :
a) Air cooled top / side discharge condensing unit with single / multiple inverter scroll compressor
b) Evaporators of various type indicated compatible to VRF system
c) Refrigerant kits for condensing unit and evaporators
d) Refrigerant piping and control cabling (to be measured and paid separately)
e) Enclosures as specified and suitable for the location
f) Mounting brackets / platform for condensing unit
g) Brackets and supports for evaporator units
h) Vibration isolators where ever required
1.1 | VRF Condensor / Outdoor Units
Supply, installation and testing of VRF based Top / Side discharge Condensers / Outdoor units as specified and shown on the drawing
a) Mounting brackets/platform
b) Brackets and supports
c) Vibration isolators where ever required
a) Outdoor condition : DB : 40 deg.C, MCWB : 22 deg.C
b) Indoor condition : DB : 20 to 24 deg.C, RH : No control
c) Type : Air cooled condensing unit in twin module
d) Compressor Type : Inverter Scroll
e) Minimum EER
1.1.1 | VRF Side Discharge Outdoor Units
a | 6.0 HP | Nos. |  |  | 0
b | 8.0 HP | Nos. | 1 |  | 0
c | 10.0 HP | Nos. |  |  | 0
1.2 | VRF Evaporator / Indoor Units
Supply, installation and testing of VRF based Evaporators / Indoor units as specified and shown on the drawing
a) Mounting brackets/platform
b) Brackets and supports
1.2.1 | VRF Standard Cassette Units (Size : 900 x 900) with Decorative Panel
a | 1.50 TR, 650 cfm (with In-built Drain Pump) | Nos. |  |  | 0
b | 2.00 TR, 750 cfm (with In-built Drain Pump) | Nos. |  |  | 0
c | 2.50 TR, 800 cfm (with In-built Drain Pump) | Nos. | 2 |  | 0
d | Aldes Connection for Fresh Air Supply | Nos. | 2 |  | 0
1.3 | CONTROLLERS
1.3.1 | Cordless Remote Controller (Handset type) | Nos. |  |  | 0
1.3.2 | Corded Central Remote Controller (Wall/Ceiling mounted) | Nos. | 1 |  | 0
| TOTAL FOR I |  |  |  | 0
II | AIR DISTRIBUTION
Design, supply, fabrication, installation of air distribution system as specified and shown on the drawing complete with :
a) GI sheet metal ducting
b) All control and safety dampes and actuators
c) Supply and return air outlets
d) Gravity louvers and bird screen
e) Supports and hangers and fixing materials
f) Thermal and acoustic insulation
2 | SHEET METAL DUCTING
Factory fabricated sheet metal ducting conforming to SMACNA standard complete with :
a) GI sheet having 120g/sq.m zinc coating and thickness to suit the pressure rating and duct size
b) Air tight joints with low VOC sealent
c) Accessories such as spliter damper, guide vanes etc.
d) Access doors at strategic location for duct internal cleaning
Note :
Duct size indicated are clear internal dimensions for the air passage. The sheet metal duct to be increased proportionately where internal acoustic lining is provided
2.1 | Fresh Air Rectangular Duct
a | 26 G - 0.40 mm with C&S joints for ducts upto 600 mm | Sq.m. |  |  | 0
b | 24 G - 0.56 mm with TDF joints for ducts 610 to 750 mm | Sq.m. | 8 |  | 0
c | 22 G - 0.63 mm with TDF joints for ducts 760 to 1000 mm | Sq.m. |  |  | 0
0
2.2 | Supply Air Rectangular Duct
a | 26 G - 0.40 mm with C&S joints for ducts upto 600 mm | Sq.m. |  |  | 0
b | 24 G - 0.56 mm with TDF joints for ducts 610 to 750 mm | Sq.m. |  |  | 0
c | 22 G - 0.63 mm with TDF joints for ducts 760 to 1000 mm | Sq.m. |  |  | 0
2.3 | Flexible Circular Duct with Insualtion
Factory fabricated non flamable multi layered flexible ducts compliant to AWTA Fire Standard complete with :
a) 3 ply polyster laminated aluminium foils bonded together through low VOC synthetic adhesive
b) Corrosion proof carbon spring wire sandwiched between the foils
c) 25 mm 32 kg/m3 glass fibre insulation with polyster laminated aluminium foil wrapping
d) End fittings / clamps
a | 100 mm diameter duct | Rmt | 2 |  | 0
b | 150 mm diameter duct | Rmt |  |  | 0
3 | VENTILATION UNITS
Supply, installation,testing and commissioing of ventilation units cabinet type as specified and shown on the equipment data and drawings complete with :
a) Centrifugal fan with motor and drive assembly
b) Filter assembly with plenum
c) Base frame and anti vibration mounts
3.1 | Inline Fans
Supply, installation, testing and commissioning of inline fans of circular / rectangular complete with :
3.1.1 | Circular Inline Fresh Air Fan with filter & Birdscreen protection
a | 150 cfm, 15mm wg st.pr. | Nos. | 1 |  | 0
b | 350 cfm, 18mm wg st.pr. | Nos. |  |  | 0
4 | AIR CONTROL DEVICES
The air control devices for controlling and balancing the air distribution system as specified and shown on the drawing excluding splitter dampers and guide vanes, which are part of ductng work complete with :
a) GI sheet metal frame of adequate thickness and strength to suit the size with stoppers and seats
b) GI control blades suitable for the duty and application
c) Necessary linkage axle, bearing, handle etc.
d) Locable quadrant (with extended rod for insulated duct) liver with pointer for damper position for manual volume control dampers
e) 24/220V damper actuator for motorised dampers
4.1 | Volume Control Dampers
Manually operated volume control dampers complete with :
i) Mounting frame : 150 x 1.2 mm profiled with flange
ii) Damper blades : 0.7 mm multi leaf airofoil opposed blades
iii) Linkage & axle : Suitable for the damper size
4.1.1 | Volume Control Damper for AC system | m2 |  |  | 0
4.1.2 | Volume Control Damper for Fresh Air system | m2 |  |  | 0
4.1.3 | Collar / Grille Damper | m2 |  |  | 0
5.2 | Air Outlets
Selection, supply, installation, testing and commissioning of Aluminium powder coated grilles and diffusers as specified and shown on the drawing to meet the air quantity indicated, uniform air distribution and noise level not exceeding 30 NC complete with :
a) Heavy gauge extruded aluminum bars for grilled and punched sheets for diffusers
b) 25mm wide margin frames
c) Uniformly spaced deflectors
d) Concealed fixing arrangements
e) Opposite blade volume control dampers for supply air with concealed adjusting key hole
Notes :
1) Size indicated are clear opening without margin frame
2) Outlets of less than 0.1 sq.m shall be mesured as 0.1 sq.m
5.2.1 | Linear Grilles
a) Margin frame on longitudinal sides
b) Aeroline extruded bars of 0°, 15° or 30° spaced at 12.5 mm
c) Vertical interlocked spacers
d) Volume control dampers wherever required
a | Linear Grille - 150mm wide | m2 |  |  | 0
5.4 | Flexible Connection
Supply, fabrication, installation, testing and commissioning of flexible connections at the air handling equipments and building expansion joints complete with :
a) 150 mm long fire resistant double layer canvas capable of withstanding 93 deg.C
b) 80 x 0.9mm GI strip secured at both ends
c) Flanged joints at AHE and distribution ducting
5.4.1 | AC Canvas Connection | Nos. |  |  | 0
5.4.2 | Ventilation Canvas Connection | Nos. | 2 |  | 0
6 | SUPPORTS & STANDS
| Supply, fabrication, installation at the proposed location of MS base frame / platform for installing outdoor units duly epoxy coated complete with vibration isolation pads, supports, etc. | Kg | 25 |  | 0
7 | PIPING & CONNECTIONS
7.1 | Refnet Joints
| Supply, installation, testing & commissioning of Refnet joints connecting refrigerant pipes of required sizing : | Nos. | 2 |  | 0
7.2 | Refrigerant Pipe + Insulation
All refrigerant piping between indoor & outdoor Units duly insulated and covered with Al. foil as per specifications. All piping inside the room shall on MS Ladder type. Pipe line must be tested for requisite pressure & must be supported. All refrigerant piping to be insulated with 19 mm thick class "O" armaflex nitrile rubber with UV protection as per manufacturer.
a | Copper piping with required sizes and insulation | Rmt | 65 |  | 0
7.3 | Drain Pipe + Insulation
Drain Piping Supply, installation, testing & commissioning of Insulated drain piping of C-PVC type including all fittings, bends, flanges, and accessories etc. & 9mm thick hitlon pipe insulation covered with 50mm wide masking tape.
a | 25mm diameter pipe | Rmt | 17 |  | 0
b | 32mm diameter pipe | Rmt |  |  | 0
c | 40mm diameter pipe | Rmt |  |  | 0
7.4 | Cable Trays
Supply and fixing of following size hot dip GI perforated ladder type cable tray made out of 2mm thick GI sheet including MS supports for fixing the tray, anchor fasteners and including 2 runs of 25 x 5 mm GI strip along with cable tray etc. complete as required
a | 50 mm high, 100 mm wide, Perforated type tray | Rmt | 22 |  | 0
b | 50 mm high, 150 mm wide, Perforated type tray | Rmt |  |  | 0
7.5 | Refrigerant Gas
| Testing & Commissioning charges along with topping-up of refrigerant gas | Kg | 20 |  | 0
| TOTAL FOR II |  |  |  | 0
III | INSULATION
Supply and fixing of insulation for HVAC installation as specified and shown on the drg. complete with :
a) Insulation material specified
b) Low VOC bonding materials
c) Vapour barrier and clading materials
d) Fixing and binding materials
8 | INTERNAL / EXTERNAL INSULATION
8.1 | DUCT ACOUSTIC INSULATION
Acoustic insulation of ducting and roof complete with :
a) Open cellular, anti-microbial nitrile rubber insulation of density 50 kg/cu.m
b) Synthetic bonding material
c) Stick pins, fixing screws and nuts
Internal Acoustic lining of supply & return ducting of following thickness
a | 13 mm | m2 |  |  | 0
b | 19 mm | m2 |  |  | 0
8.2 | DUCT THERMAL INSULATION
Thermal insulation of HVAC installation with :
a) Refrigerant piping : Tubes
b) Air distribution ducts : Sheets
c) Equipments : Sheets
d) Exposed roof & walls : Sheets
e) Provision for easily dismantable at flanged joints, valves, dampers and other control system
Nitrile Rubber
a) Close cellular nitrile rubber of thickness indicated, having 76 kg/cu.m density and 0.04 W/m °C thermal conductivity, Class I fire rating
b) Synthetic solvent bonding materials
c) Vapour barrier and mechanical protection using glass fibre cloth wrapping with synthetic solvent coating
d) Binding wires wherever required
Thermal Insulation for supply & return ducting of following thickness
a | 13 mm | m2 |  |  | 0
b | 19 mm | m2 |  |  | 0
8.3 | RETURN AIR BOXING INSULATION
a) Close cellular nitrile rubber of thickness indicated, having 76 kg/cu.m density and 0.04 W/m °C thermal conductivity, Class I fire rating
b) Synthetic solvent bonding materials
c) Vapour barrier and mechanical protection using glass fibre cloth wrapping with synthetic solvent coating
d) Binding wires wherever required
Thermal Insulation for Return Air Boxing of following thickness
a | 19 mm | m2 |  |  | 0
b | 25 mm | m2 |  |  | 0
8.4 | UNDERDECK INSULATION
Insulation of internal surface of exposed roofs & walls complete with:
a) Insulation sheet of thickness specified
b) Synthetic adhesive bonding
c) Fixing the insulation to the slab and walls at centres not exceeding 600mm using anchor plugs, screws and 50 x 50 x 0.5mm GI washers
d) Cross netting using GI wires
Underdeck Thermal Insulation of following thickness
a | 19 mm | m2 | 60 |  | 0
b | 25 mm | m2 |  |  | 0
| TOTAL FOR III |  |  |  | 0
IV | ELECTRICAL
Supply, installation, testing and commissioning of Electrical work connected with the Cooling water system complete with :
a) Power panels and switchgears
b) Power and control cabling
c) Earthing
Note :
All electrical items furnished below is guidelines. The offer to be in accordance with the electrical load of equipment supplied
9 | MCB & ELCB for VRF ODU's | Nos. | 1 |  | 0
10 | STARTER PANELS & SWITCHGEARS
Supply,installation,testing and commissioning of floor mounted free standing totally enclosed and compartmentalised cubicle panel as specified and shown on the drawing complete with IP 65 enclosure suitable for outdoor installation consisting of :
a) R,Y,B & N tinned copper busbar of adequate capacity duly tapped for incoming and outgoing feeders mounted over insulated supports
b) Incoming and outgoing feeders, starters and control equipments mounted in isolated compartments
c) Interconnections and wiring
d) Connector blocks for incoming and outgoing cables
e) Internal copper earth busbar of adequate rating with 2 nos. M10 brass studs and washers
f) Protection relays and contactors
g) Measuring instruments and indicating lamps
h) Current transformers wherever required
i) Protection fuses for measuring instruments and indicating lamps
j) Structural steel frame work and base frame
k) 2 mm CRCA sheet steel enclosure with compart- mentalisation for busbar cable and individual feeder, interlocked hinged doors for individual compartment
l) Adequate vermin proof ventilation opening in the enclosure
m) Feeder and compartment identification labeling with rating
n) Gland plate for cable entry
o) Anticorrosive treatment for all structural steel and CRCA sheet work through 7 tank or equivalent process
p) 2 coats of oven baked epoxy coating of approved shade
q) Anchor bolts and fixing accessories
10.1 | Starter Panels
Supply, installation, testing and commissioning of Starter Panels complete with fixing accessories as per requirement & as mentioned:
a) Dust, damp and vermin proof free factory built
b) Sheet steel enclosed non-draw out modular type wall mounted starter
c) powder coated as per specifications
d) including 5 RMT cabling, earthing
e) including necessary accessories from starter to Unit
f) include following outgoing feeder
a | Single Phase, 0.3 Kw - VRF Cassettes & Fresh Air fan | Nos. | 1 |  | 0
b | Three Phase, 7.0 Kw for VRF Side Discharge Mini ODU | Nos. | 1 |  | 0
10.2 | Switchgear
| Supply, installation, testing and commissioning of switchgears in 16 gauge MS painted enclosure complete with fixing accessories termination earthing etc. for VRF ODU's | Nos. | 1 |  | 0
11 | CABLING
11.1 | Power Cable
Supply, Laying and Terminating Power Cabling for the HVAC equipments as specified and shown on the drawing complete with :
a) 1100V Multicore PVC insulated sheathed and armoured aluminum / copper cables
b) Cable Lugs and Glands and termination
c) Aluminum Perforated Cable Tray
d) Cable Clamps and fixing materials
a | Suitable Cable | Rmt. | 10 |  | 0
11.2 | Control / Communication Cable
Multicore control cabling for automatic operation and control of HVAC equipments including termination, ferruling etc.
a | Suitable Cable | Rmt. | 48 |  | 0
11.3 | Earthing Cable
Supply, laying and interconnecting earthing conductors as specified and shown on the drawing complete with :
a) Earth conductor with protective coating
b) Excavation and back filling
c) Clamps and saddles
a | 50 x 3 mm GI | Rmt. | 25 |  | 0
| TOTAL FOR IV |  |  |  | 0
V | MISCELLANEOUS
12 | SMOKE TEST
a | Smoke Tests for all supply, fresh & exhaust air ducts in all areas. | Lot |  |  | 0
| TOTAL FOR V |  |  |  | 0